## Gas_Lines_Model
GAS LINES FLOW MODEL
Name of Gas Line Run | Test for Gas Lines
Inputs
Pipeline Diameter | 150 | mm
Wall Thickness | 15 | mm
Pipeline Length | 10700 | m
Operating Pressure | 80 | bar
Gas Temperature | 87 | deg. C
Pipeline Material | X80
Gas Mol Weight | 19.13 | kg/kmol
Heat of Combustion | 40700 | kJ/kg
Reaction Time | 2 | s
Escape Velocity | 2 | m/s
Calculated Results
Full Bore Release Rate (Immediate) | 335.9043 | kg/s
Full Bore Release Rate (Delayed) | 19.8424 | kg/s
Maximum Hole Size | 75 | mm
Maximum Hole Release Rate | 47.6969 | kg/s
Distance (m) to Fatality Rate
| Ignition Probability | Event Frequency | 100% | 50% | 1%
Full Bore Fire Ball (Immediate) | 0.033387 | 1.0266e-10 | 23.759 | 23.759 | 24.001
Full Bore Fire Ball (Delayed) | 0.0034627 | 1.0648e-11 | 9.001 | 9.001 | 18.001
Maximum Hole | 0.0069907 | 2.4363e-10 | 5.001 | 11.001 | 21.001

## Gas_Lines_Data
Name | Test for Gas Lines
Diameter | 150 | mm
Operating pressure | 80 | Bar
Wal thickness | 15 | mm
Length | 10700 | m
Mole weight gas | 19.13 | kg/kmol
Temperature gas | 87 | ⁰C
Hcomb | 40700 | kJ/kg
Reaction time | 2 | s
Escape velocity | 2 | m/s
Material | X80
Release rate FB imm | 335.9043 | kg/s
Release rate FB delayed | 19.8424 | kg/s
Release rate hole | 47.6969 | kg/s
Max hole size | 75 | mm
Summary
|  |  | 3200TDU | 2000TDU | 1000TDU | Step
| Ignition prob | Ingnited Freq | 100% | 50% | 1%
FB Immideate fire ball | 0.033387 | 1.0266e-10 | 23.759 | 23.759 | 24.001 | 12
FB delayed | 0.0034627 | 1.0648e-11 | 9.001 | 9.001 | 18.001 | 9
Hole | 0.0069907 | 2.4363e-10 | 5.001 | 11.001 | 21.001 | 1